Compact Control Valve Actuator

User Technical Specification

25 June 2015

## Section 1	Actuator Systems

- Seller shall be responsible for correctly sizing the actuator based on the process operating conditions and characteristics of the control valve. Sizing shall ensure that a 25% safety factor for torque or thrust is provided.

- The actuator will be a single phase AC powered electric actuator, capable of delivering sufficient thrust or torque to operate at the required speed for the applicable process. Alternatively, when requested on the data sheets the actuator may need to accept a 24 VDC supply.

- The safety margin of motor power available for seating and unseating the valve shall be sufficient to ensure torque/thrust limit trip at maximum valve torque with the supply voltage 10% below nominal.

- Actuator must be capable of continuous modulation.

## Section 2	Materials or Construction

- The actuator body will be constructed of cast aluminum.

- The enclosure will be IP67.

## Section 3	Performance

- Performance parameters must all be as follows:

| Linearity | 1.0% |  |
| --- | --- | --- |
| Deadband | 0.00% to 10.0% | Adjustable |
| Repeatability | 0.5% |  |
| Hysteresis | 0.70% |  |
| Resolution | 0.2% | Linear, Quarter-turn |
| Resolution | 2 degrees | Multi-turn |

## Section 4	Actuator/valve Yoke

- Yoke assemblies are to be supplied, when requested, with the actuator and shall provide rigid support, not only static support for the actuator, but to preclude any flexing during rapid operation.

## Section 5	Manual Hand Wheel

- As standard, a knob for manual operation of the actuator shall be provided such that the maximum knob operating torque shall not exceed 30 lbf.in.

## Section 6 	HMI and Set up

- A method setting of actuator and option configurations must be provided.

The facility to adjust the force or torque seating of the valve must be selectable on the HMI. Settings such as max torque, dead band etc, shall be configured using push button switches located on the main PBC.  An LCD display will be used to view the actuator configuration parameters including:

6.1.1 POSITION: Actuator Position.

6.1.2 SETPOINT: Actuator set point.

6.1.3 TORQUE/THRUST (Dependent on Model). Value to be adjustable between 50 and 100 % of rated value.

In addition, a shut off torque or thrust of approximately 150% of the rated value must be available and configurable using the HMI.

6.1.4 LOCAL/REMOTE MODE: The actuator to be configurable for either LOCAL or REMOTE operation.

6.1.5 MANUAL JOG: The actuator to be available for HMI pushbutton control operation when selected to ‘LOCAL’ operation.

6.1.5 CLOSE LIMIT: Set the closed limit of travel.

6.1.6 OPEN LIMIT: Set the open limit of travel.

6.1.7 COMMAND SIGNAL 4/20 SET UP: Input signal field calibration for remote positioning control.

6.1.8 DEADBAND: Adjustment of the minimum input signal step change required for movement between 0 to 10%.

6.1.9 STATUS INDICATION: The actuator status to be monitored in both Local and Remote control modes.

6.1.10 FAULT HISTORY: Alarms and Faults are to be stored and listed by event number and type.

6.1.11 SPEED: The actuator operating speed must be adjustable down to 50% of the maximum speed in increments of 1%.

- Local Controls

The actuator shall incorporate, as an option, local controls for Open/Close and a Local/Stop/Remote mode selector switch lockable in the following three positions: local control only, stop (no electrical operation), remote control plus local stop only. It shall be possible to select maintained or non-maintained local control.

The selector switch will be designed in such a way as not to allow the ingress of water.

## Section 7	Position and availability Indication

- Continuous remote position indication in the form of a 4-20mA output shall be provided as standard.

- A non-contacting absolute encoder shall be used to determine the actuator’s position.

- Two programmable relays shall be provided to indicate actuator availability status and/or valve position.

- The actuator must be capable of positioning using a 4-20mA control signal either full range or split range configuration.

- Where specified and shown on the plan drawings, digital fieldbus communications cards will be supplied to facilitate control & indication as well as other communications needs. Compatible optional cards will include HART, Profibus, Foundation Fieldbus, Modbus, DeviceNet and Pakscan.

## Section 8	Auxiliary input/output options.

- An optional auxiliary card shall be available to allow the following:

  - Four programmable inputs to facilitate:

    - Open and close digital inputs for remote control.

    - Maintain/Stop input to accommodate either maintained or “push to run” digital signals and provide stop functionality.

    - A separately terminated ESD signal (independent from “loss of signal” fail to position).

  - Four programmable output relays to facilitate indication of:

| Function | Description |
| --- | --- |
| No Function | Always de-energized to reduce power consumption |
| Intermediate position indication | Active if the actuator passes an intermediate position (open or close direction) |
| General Fault | General fault detected. Stall Open/Close, Over Torque/Thrust-Open/Close, Loss of Comms, or Loss of Command. |
| Loss of Demand Signal | Active when the demand signal is lost |
| Loss of Feedback Signal | Active when the feedback signal is lost |
| Motor Stalled in Open Direction | Active when the motor fails to move after a valid open command has been sent |
| Motor Stalled in Closed Direction | Active when the motor fails to move after a valid close command has been sent |
| Open Torque/Thrust Overload | Active when the opening thrust / torque (at any position) reaches the configured value |
| Close Torque/Thrust Overload | Active when the closing thrust / torque (at any position) reaches the configured value |
| Over Temperature | Active when temperature is over limit. |
| Loss of Bus Communications | Active when communications signal is lost |
| Local Selected | Active when LOCAL mode is selected |
| Closed Position Limit | Active when the actuator is at Fully Closed position |
| Open Position Limit | Active when the actuator is at the Fully Open position |
| Emergency Shutdown Active | Active when an ESD signal is present |
| Critical Fault | Critical Fault detected -Actuator disabled. Loss of Feedback EEPROM fault |
| Dither | Active if the output exceeds 2000 1% position changes per hour. Output dither. |
| Monitor Relay Active (Available) | Active when the actuator is available for remote control - selector set to REMOTE and no faults present that would inhibit operation (General or Critical Fault). |

  - Relays to have a rating of 3 Amps, and switching power of 60W inductive and 150W resistive.

  - The contact form for all auxiliary inputs and outputs shall be configurable to suit normally open or normally closed system philosophy.

Section 9 	Environment and enclosure

- Actuator shall be capable of functioning in a normal ambient environmental temperature of:

EP Product: -4 to +149 °F (-20 to 65 °C).

WT Product: -22 to +158 °F (-30 to 70 °C).

Local Controls and reserve power pack product: -4 to +140°F (-20 to +60 °C)

- Actuators shall be 'O' ring sealed, watertight to IP67.

- Enclosure must allow for temporary site storage without the need for electrical supply connection.

- All external fasteners shall be stainless steel as standard.

- Where specified, actuators shall be certified for explosion/hazardous applications by the appropriate certifying body.

Section 10 	  Power or signal failure mode.

- Should the control signal be lost, the actuator must have a means of running to a pre-configured position or remaining at the last position.

- This pre-configured position must be easily programmable using the HMI pushbuttons. No physical change to the build or construction of the actuator shall be needed to achieve the change in fail position.

- The actuator will, as an option, include a reserve power pack, utilizing an internal reserve power pack to provide a reliable means of positioning the valve to a safe position on loss of power supply or emergency shutdown (ESD) signal. The actuators can be fail to close or open dependent on the criteria of the process. Position indication should be available during power loss action via a built in LCD display. This should show actuator position, critical and non-critical fault symbols plus additional reserve power pack status.

Section 11 Start-Up Kit

- Each actuator shall be supplied with a startup kit comprising installation instruction, electrical wiring diagram and sufficient spare seals to make good any site losses during the commissioning period.

Section 12 Performance Test Certificate

- Each actuator must be performance tested prior to leaving the manufacturing factory.  Individual test certificates shall be created and supplied free-of-charge.  The test equipment should simulate a typical valve load and the following parameters should be verified:

- Torque or thrust at maximum setting

- Torque or thrust at minimum setting

- Speed and travel

- Input command calibration at 0% and 100%

- Output position calibration at 0% and 100%

- In addition, the test certificate should record details of specification, such as options, wiring diagram code number, model number and power supply voltage.

Section 13 Warranty

- Each actuator shall be warranted for a minimum of 12 months of operation from date of shipment. This warranty shall be held in effect regardless of pre-commissioning conditions in a typical indoor or outdoor environment as long as the actuator is not abused, disassembled or conduit plugs removed. This warranty shall not require the use of special storage procedures (such as the use of indoor storage, plastic bags, desiccants, and the connection of heaters) in order to be maintained.

- The warranty shall be extended to 24 months from the date of start-up if the actuator is set up and started up by a factory-trained Field Service Technician employed by the actuator manufacturer.